## Slide 1: Modeling and Valuation of Pumped Storage Hydropower Resources
Majid Heidarifar, EPRI
Nikita Singhal, EPRI
Aidan Tuohy, EPRI
Russ Philbrick, Polaris
Erik Ela, EPRI
Pablo Ruiz, NewGrid
June 23, 2021
This presentation is, in part, supported by the U.S. Department of Energy, Water Power Technologies Office under Award Number DE-EE0008783 Predicting Unique Market Pumped Storage Significance (PUMPSS)
FERC Technical Conference

## Slide 2: Pumped Storage Hydro Power Resources
By far the largest storage resource in the current electric grid
  Fast Ramping Capability
  Energy and AS provision
  Help in both shortage and surplus conditions (pumping and generation)
Traditional Design not as flexible
  Discrete operating range: block loaded especially in pumping mode
    Need commitment decisions
    Can have big impact on congestion
  Historically there has not been a need for optimization because of predictable charge/discharge times
Disclaimer: “This presentation was prepared as an account of work sponsored by an agency of the United States Government. Neither the United States Government nor any agency thereof, nor any of their employees, makes any warranty, express or implied, or assumes any legal liability or responsibility for the accuracy, completeness, or usefulness of any information, apparatus, product, or process disclosed, or represents that its use would not infringe privately owned rights. Reference herein to any specific commercial product, process, or service by trade name, trademark, manufacturer, or otherwise does not necessarily constitute or imply its endorsement, recommendation, or favoring by the United States Government or any agency thereof. The views and opinions of authors expressed herein do not necessarily state or reflect those of the United States Government or any agency thereof.”
Disclaimer: This presentation includes draft results that are subject to change.

## Slide 3: State of the Art
PSH presently participates in majority of ISO products
  Offer as separate pump/generator participants
  PJM – Hydro optimizer, optimizes mode of operation to minimize cost and ensure SOC targets
FERC Order 841: ISO/ RTO design proposals implementation details
Order 841 Aspect | NYISO | PJM | SPP | ISO-NE | MISO | CAISO
Participation Model | Most entities have proposed two separate participation models: Continuous (e.g., batteries) and discontinuous (e.g., PSH) models Rationale: ESRs are continuously dispatchable; PSH resources have forbidden operating regions that need to be accounted for appropriately ESRs can participate in energy, AS, and capacity markets (wherever applicable) Rationale: Requirement from FERC Order 841 |  |  |  |  | 
 | ESRs and ELRs; PSH cannot submit a charge and discharge offer in the same hour | ESRs; PSH plants can still use pumped hydro optimizer | MSRs; PSH plants cannot submit a charge and discharge offer in the same hour | CSFs and BSFs (for PSH) | ESRs (also supports PSH) | NGRs and PSH model
AS: Ancillary Service; BSF: Binary Storage Facility; CSF: Continuous Storage Facility; ELR: Energy Limited Resource; ESF: Energy Storage Facility; ESR: Electric Storage Resource; MSR: Market Storage Resource; NGR: Non-Generator Resource; PSH: Pumped Storage Hydro; SOC: State of Charge

## Slide 4: Overall Project Objectives
Attain a Deeper Understanding of the Value of PSH
Goal: Develop a framework and outline the parameters needed to analyze the energy and ancillary services pumped storage hydropower (PSH) provides to the electricity grid currently and how that value may change as the generation asset mix, especially as it relates to increased penetration of variable renewable energy (VRE), on the grid changes over time.
  Demonstrate current state-of-the-art in modeling of PSH operation
  Improve state-of-the-art modeling approaches to better capture value of provision of certain essential reliability services (e.g., ramping, regulation, etc.) coming from PSH
  Examine the value of different PSH technologies/configurations (e.g., traditional site-specific design, variable speed) and C rate (MWh/MW ratio) to better understand which technologies and storage durations may provide the most value
  Determine the optimal configuration of PSH technology (i.e., capabilities and C rate) that maximizes PSH economic and system resilience and reliability value given existing market structures at current and anticipated future VRE penetrations

## Slide 5: Modeling Approach

## Slide 6: Southeast Utility Operations
*DASCUC is run at 7AM on the current operating day due to less stressed conditions from midnight – 7am (ISOs/RTOs typically run their DAM at 11AM on the previous operating day or midnight), and run to end of 7 days out
The model is set up as illustrated in the figure, with a week-ahead run that is updated daily and simulated for every morning using updated information. Hourly ‘actuals’ will then be used for wind, solar, and load in the real-time run to ensure the impact of uncertainty is adequately captured in the model.

## Slide 7: PSH Facilities Modeling Approach in PSO
Enhanced Model
(multiple injectors)
(Ƞ1)
(Ƞ2)
(Ƞ3)
(Ƞ4)
Ƞ efficiency
+
-
G
L
G
L
G
L
Generator
recharge
loss
Load (pump)
Notes: The pumps and turbines were then connected to the upper reservoir. Lower reservoir not modeled explicitly, assuming that its capacity and level would not limit or impact their operation.
Each PSH facility is modeled as four pumps and four turbines (i.e., eight injectors in total for each PSH). This separation allows for the enforcement of commitment constraints on individual turbine/pumps.
The total capacity mix by fuel type for the Southeast Utility system includes ~1,539 MW of conventional hydro resources, ~2,180 MW of PSH resources, ~3,085 MW of VREs (about 7.6 GW of VRE), and ~33,703 MW of conventional generation (steam, coal, combined cycle, combustion turbines). The physical and operating characteristics of the PSH resources were obtained and represented within the PCM in an accurate manner. The EPRI team has tested and validated the newly introduced Water Resources (WR) library in PSO in the past year. Note that the WR library was introduced to model PSH resources more accurately.

## Slide 8: Southeast Utility: PSH Facilities Modeling Approach
PSH 1
Upper reservoir: 20,000 MWh
SSOC = TSOC = 10,000 MWh
Roundtrip efficiency: 80%
PSH 2 modeled as four pumps and four turbines (i.e., eight injectors in total)
  Turbines: 170 – 195 MW
  Pumps (block-loaded): Off (0 MW) and On (205 MW)
  Simultaneous pumping and generation allowed, but restricted to specific combinations of pumps and turbines
Upper reservoir: 25,000 MWh
SSOC = TSOC = 12,500 MWh
Roundtrip efficiency: 80%
PSH 1 modeled as four pumps and four turbines (i.e., eight injectors in total)
  Turbines: 250 – 350 MW
  Pumps (block-loaded): Off (0 MW) and On (308 MW)
  Pumps and turbines not allowed to operate simultaneously
PSH 2
SSOC: Start State of Charge; TSOC: Target State of Charge;
Initial storage levels in day-ahead were adjusted using the real-time cycle’s (i.e., the last cycle’s) results
Disclaimer: Assumed specifications in the model.
L
G
G
G
pipe
river
G
L
L
L
Upper reservoir
Lower reservoir
Notes: The pumps and turbines were then connected to the upper reservoir. Lower reservoir not modeled explicitly, assuming that its capacity and level would not limit or impact their operation.
Each PSH facility is modeled as four pumps and four turbines (i.e., eight injectors in total for each PSH). This separation allows for the enforcement of commitment constraints on individual turbine/pumps.
The total capacity mix by fuel type for the Southeast Utility system includes ~1,539 MW of conventional hydro resources, ~2,180 MW of PSH resources, ~3,085 MW of VREs (about 7.6 GW of VRE), and ~33,703 MW of conventional generation (steam, coal, combined cycle, combustion turbines). The physical and operating characteristics of the PSH resources were obtained and represented within the PCM in an accurate manner. The EPRI team has tested and validated the newly introduced Water Resources (WR) library in PSO in the past year. Note that the WR library was introduced to model PSH resources more accurately.

## Slide 9: Southeast Utility Operations: Scheduling Process
Day-Ahead
Includes 6-day look-ahead
Real-Time
Includes 6-hour look-ahead
Jan. 4
Jan. 5
Jan. 6
Jan. 7
Jan. 8
Jan. 9
Jan. 10
Forecast CD
Forecast 1D
Forecast 2D
Forecast 3D
Forecast 4D
Forecast 5D
Forecast 6D
Jan. 4
Actuals
Day-Ahead
Real-Time
Jan. 5
Actuals
Jan. 5
Jan. 6
Jan. 7
Jan. 8
Jan. 9
Jan. 10
Forecast CD
Forecast 1D
Forecast 2D
Forecast 3D
Forecast 4D
Forecast 5D
Jan. 11
Forecast 6D
Cluster 1
Cluster 2
Rolling Horizon
End of
Horizon
End of
Horizon

## Slide 10: Proposed Case Studies
Study Region
Current Mix
Moderate VRE Mix
High VRE Mix
Operational Sensitivities
Storage SOC
Technology Sensitivities
Operational Sensitivties
AS Req*
Provision of AS
Technology Sensitvities
C-Rate*
VSG
Operational Sensitivities
Technology Sensitivities
Storage SOC
AS Req*
RT Correction
Provision of AS
C-Rate*
VSG
Resource Sensitivities
Electrification Case
Additional Retirement*
Fuel price*
Commitment Decisions
VSG
Simultaneous Pump/Gen
C-Rate*
Notes: Base case includes about 3 GW of VRE, moderate case about 7.6 GW of VRE and high case about 20 GW of VRE. 3 GW of VRE corresponds to about 8.18% of instantaneous peak demand and about 6.88% of installed generation capacity. 7.6 GW of VRE corresponds to about 20.73% of instantaneous peak demand (in MW) with no load growth and about 15.77% of installed generation capacity. There is no wind in the Southeast Utility. 20 GW of VRE corresponds to about 54.54% of instantaneous peak demand (in MW) with no load growth and about 33% of installed generation capacity.
Adjustable Speed Generator sensitivity (e.g., eliminate the minimum pumping and generation constraints): Have soft agreement from GE to provide data.
Storage duration sensitivity (e.g., purposely add a few days with renewables being unavailable and observe the benefits of longer storage duration)
Reservoir value management sensitivity in the Southeast Utility. This is an operational sensitivity. The Southeast Utility, being a vertically integrated utility, owns the asset and so doesn’t have bidding strategies. Instead, there is the option to manage the level of water in the reservoir at the end of the operating week/day or real-time operating horizon in addition to its value. Therefore, the target state of charge/reservoir level (and potentially the opportunity costs to deviate from this target) will be varied in this scenario for the different VRE levels.

## Slide 11: Modeling Results

## Slide 12: System Characteristics
Chart: Current VRE MIX
| Oil (CT) | Coal | Solar | Ngas (CT) | Ngas (CC) | PSH (Gen) | Hydro | Nuclear | Ngas (CG)
 | 0.0088253 | 0.20818 | 0.076064 | 0.1999 | 0.13682 | 0.053741 | 0.037939 | 0.27333 | 0.0052015
Chart: MEDIUM VRE MIX
| Oil (CT) | Coal | Solar | Ngas (CT) | Ngas (CC) | PSH (Gen) | Hydro | Nuclear | Ngas (CG) | ESR (Discharge)
 | 0.0077044 | 0.023888 | 0.15194 | 0.28186 | 0.20008 | 0.052941 | 0.03312 | 0.20089 | 0.0045409 | 0.043042
 | Current VRE Mix | Medium VRE Mix
Installed Capacity (GW) | 40.6 | 46.5
Peak RT Load (GW) | 33.1 | 37.8

## Slide 13: Modeling Results: Sensitivity Analysis (Current VRE Mix)
Five Sensitivity Analysis Cases
  Case 1: Base Case
    Nomogram constraints to prevent simultaneous gen. and pumping
    Limited Dispatchability Range
    Adjustment of DA SOC based on latest RT information
    PSH recommitment in RT
  Case 2: No PSH nomogram constraint
  Case 3: Increased Dispatchability Range (50%)
  Case 4: No Adjustment of DA SOC
  Case 5: PSH Commitment fixed in DA

## Slide 14: Modeling Results: Sensitivity Analysis (Current VRE Mix)
 | Total RT Cost ($MM) | % Cost Change
Case 1: Base Case* | 249.7 | -
Case 2: Simultaneous gen/pump allowed | 249.6 | -0.06%
Case 3: Variable Speed Technology (50%) | 248.8 | -0.36%
Case 4: No Adjustment of DA SOC | 250.3 | +0.21%
Case 5: PSH Commitment Fixed in DA | 251.6 | +0.73%
* Disallows Simultaneous gen/pump is not allowed, Fixed Speed Technology, Adjusts DA SOC based on RT telemetry, Allows PSH recommitment in RT
Period of study: July 1st – 31st, 2019
Disclaimer: Assumed test case. Results may not reflect exact operations.

## Slide 15: Modeling Results: Total Real-time Energy Cost
PSH reduces the total energy production costs by 2.7% (11.3%) in current (medium) solar penetration scenarios
 | Current VRE Mix |  | Medium VRE Mix | 
 | With PSH | Without PSH | With PSH | Without PSH
RT Cost ($MM) | 249.7 | 256.5 | 205.6 | 228.8
% Cost Increase | - | 2.7% | - | 11.3%
Period of study: July 1st – 31st, 2019
Disclaimer: Assumed test case. Results may not reflect exact operations.

## Slide 16: Generation Dispatch Profile in RT (Current VRE Mix)
No PSH
w/ PSH
Chart: Hour
Chart: Hour

## Slide 17: Cleared RT Reserve Profile (Current Penetration)
Chart: Contingency Reserve
Chart: Regulation Up
Chart: Total Upward Reserve
Notes: ADD Figures from Russ’s presentation

## Slide 18: Cycling of Thermal Generators (Current VRE Mix)
 | Coal | Ngas (CC) | Ngas (CT) | Oil (CT) | PSH (Gen) | PSH (Pump)
w/ PSH | 13 | 33 | 658 | 0 | 229 | 249
w/o PSH | 18 | 42 | 1038 | 3 | 0 | 0
 | Coal | Ngas (CC) | Ngas (CT) | Oil (CT) | PSH (Gen) | PSH (Pump) | Total
w/ PSH | 0.46 | 0.36 | 2.49 | 0.00 | 0.34 | 0.00 | 3.64
w/o PSH | 0.51 | 0.46 | 3.75 | 0.09 | 0.00 | 0.00 | 4.81
Number of Startups per Technology Type
Startup Cost per Technology Type
Increased cycling of Combined Cycle and Combustion Turbine generators in absence of PSH resources

## Slide 19: Modeling Results: DA and RT PSH Schedule (Current VRE Mix)
Period of study: July 1st – 31st, 2019
Disclaimer: Assumed test case. Results may not reflect exact operations.
PSH1:
  Reservoir: 25,000 MWh
  Roundtrip efficiency: 80%
  Four pumps and four generators
    Generators: 250 – 350 MW
    Pumps (block-loaded): Off (0 MW) and On (308 MW)
    Pumps and turbines not allowed to operate simultaneously
PSH2:
  Reservoir: 20,000 MWh
  Roundtrip efficiency: 80%
  Four pumps and four generators
    Generators: 170 – 195 MW
    Pumps (block-loaded): Off (0 MW) and On (205 MW)
    Under certain combinations, simultaneous Pump and generation is allowed

## Slide 20: Modeling Results: DA and RT PSH SOC (Current VRE Mix)
Period of study: July 1st – 31st, 2019
Disclaimer: Assumed test case. Results may not reflect exact operations.

## Slide 21: Key Observations
Total energy production costs increase in absence of PSH resources (by ~2.7% in current penetration, and 11.3% in future medium penetration)
PSH reduces cycling of thermal generators (CCs and CTs)
PSH contributes considerably to RT contingency reserve, and regulation up and down reserves
Allowing simultaneous generation and pumping may not result in considerable cost savings for an uncongested system
Block loading has an increased likelihood of resulting in increased operating cost
Variable Speed Technology enhances flexible operation
There is a need to better understand how adjusting the initial SOC in the DA based on latest RT info can impact the market solution
  Example: ERCOT

## Slide 22: Other Considerations: management of water quantities
Cascading systems with time requirements for flow between reservoirs
Constraints on river flows
Impact of reservoir head and tailwater losses
G
L
L
G
G
G
inflow
loss
river
G
pipe
PSH reservoir
(integrated)
L
G
cooling
river
inflow
loss
water supply

## Slide 23
Majid Heidarifar, mheidarifar@epri.com
Nikita Singhal
Aidan Tuohy
Russ Philbrick
Erik Ela
Pablo Ruiz

## Slide 24: Order 841: State of Charge Management
Required ISO to allow self-management of SOC by ESR
Required “consideration” of SOC related parameters through bidding, telemetry, or otherwise (e.g., SOC limits, round-trip efficiency)
[1] Electric Storage Participation in Markets Operated by Regional Transmission Organizations and Independent System Operators, FERC Order 841, Final Rule, 162 FERC 61, 127 (February 15, 2018) (“Order No. 841”).

## Slide 25: ISO/RTO Design Proposals: Implementation Details
Order 841 Aspect | NYISO | PJM | SPP | ISO-NE | MISO | CAISO
State of Charge Management | Only a few ISOs are offering both ISO-SOCM and Self-SOCM. Other ISOs are offering a hybrid SOCM-Lite option. ISO-SOCM: SOC is a variable in multi-interval optimization and the ISO ensures SOC feasibility. SOCM-Lite: SOC is a parameter in sequential optimization and the ISO ensures SOC feasibility. Rationale: Requirements from FERC Order 841; SOCM option is also impacted by the market clearing software design |  |  |  |  | 
 | ISO-SOCM (excludes desired ending SOC level) and Self-SOCM (does not ensure SOC feasibility, but ISO will align schedules with telemetered SOC in the RTM); NYISO can suspend ISO-SOCM and default to Self-SOCM; PSH plants – Self-SOCM; ESRs have the option to switch b/w SOCM modes within RTM, and b/w DAM and RTM | ESRs – SOCM-Lite (ensures SOC feasibility and accounts for SOC, and SOC limits in its sequential optimization); PSH plants – ISO-SOCM | SOCM-Lite (ensures SOC feasibility in sequential optimization); can submit max daily MWh limit | SOCM-Lite (includes two new telemetered points in RT, i.e., 15-minute and 1-hour available energy and available storage, to ensure SOC feasibility in sequential optimization); ESFs can submit max daily MWh charge and discharge limits in the DAM. No SOC-specific parameters in DAM. | SOCM-Lite (ensures SOC feasibility in sequential optimization); max daily MWh limit included only for PSH plants | ISO-SOCM (excludes desired ending SOC level) and Self-SOCM (does not ensure SOC feasibility); can submit daily min and max energy limits for DAM
AS: Ancillary Service; BSF: Binary Storage Facility; CSF: Continuous Storage Facility; DAM: Day-ahead Market; DR: Demand Response; ESF: Energy Storage Facility; ESR: Electric Storage Resource; MSR: Market Storage Resource; NGR: Non-Generator Resource; POI: Point of Interconnection; PSH: Pumped Storage Hydro; RTM: Real-time Market; SOC: State of Charge; SOCM: SOC Management

## Slide 26: State of Charge Management: Options
Self-Schedule
ESR self-dispatches its output and is insensitive to price.
Self-SOC-Management
ESR provides an offer curve analogous to traditional resources.
ESRs can set offers to ensure desired and feasible SOC.
SOC-Management-Lite
ESR provides an offer curve.
ISO-SOC-Management
ESR may or may not provide an offer curve.
ISO ensures SOC feasibility and optimizes ESR schedules across time to minimize cost.
ISO does not schedule ESR if it would lead to infeasible SOC.
Schedules are not optimized across time to optimize ESR schedules.
ISO schedules without SOC consideration
Allowed by all ISOs/RTOs
CAISO, NYISO ESRs, NYISO PSH units
CAISO, NYISO ESRs,
PJM PSH units
SPP, ISO-NE, MISO, PJM
ISO Scheduling Responsibility / Theoretical Economic Efficiency and Reliability Benefits / Complexity
ESR Asset Owner Participation Responsibility and Flexibility / Computational Efficiency